## Sheet1
(1) COMPENSATED HARDNESS CALCULATOR
Enter the known paramenters in the appropriate red boxes below. Regeneration frequency is then as per the "Family member" columns. Choose a model with a frequency of 5 or greater. Also check that peak flow is sufficient for the application
Note that if the complete system includes Filox or similar pretreatement, you can reduce the Iron level (from that provided in the water test) to enter below, by approx 90% and Manganese by approx 50% NB: No insoluble Iron allowed in a softener.
Total hardness from water test | [6 empty] | 200 | 200 |  | Formulae
Hardness added by Neutraliser | [6 empty] | 0 | 0 |  | CO2 x 2
Hardness added by soluble Iron to a max of 6 ppm | [6 empty] | 0 | 0 |  | Fe x 40
Hardness added by Manganese to a max of 2 ppm: | [6 empty] | 0 | 0 |  | Mn x 120
[6 empty] | subtotal |  | 200
Safety factor from below: | [6 empty] | 1.1 | 20
|  |  | Compensated Hardness total (used below). |  |  |  |  | 220
safety factors
Compensated hardness <300, multiply by 1.1
Compensated hardness from 300 to 600 , multiply by 1.2
(2) PERFORMANCE FIGURES
Family Members |  |  |  | 2 | 3 | 4 | 5 | 6 | 7 | 8
Estimated Litres used per Day (250 L/person) |  |  |  | 500 | 750 | 1000 | 1250 | 1500 | 1750 | 2000
Hardness removed per Day (g) |  |  |  | 110 | 165 | 220 | 275 | 330 | 385 | 440
Units can be programmed for Low, Medium, or High salt. The "Medium" setting suits most applications and is used in the calculations below. It is also the default setting (5.2) in the Erie 2400 valve. For other settings request our Erie softener valve capacity chart.
APL product code. | Peak flow (lpm) | Media volume (L) | Cycle 3 (min) | 2: Days Between Regeneration (5-6 is optimal)
WS735 & CWS735 | 30 | 12 | 3 | 5.6636 | 3.7758 | 2.8318 | 2.2655 | 1.8879 | 1.6182 | 1.4159
WS840 | 40 | 18 | 2 | 10.4364 | 6.9576 | 5.2182 | 4.1745 | 3.4788 | 2.9818 | 2.6091
WS948 | 50 | 25 | 3 | 11.8455 | 7.897 | 5.9227 | 4.7382 | 3.9485 | 3.3844 | 2.9614
WS1035 & CWS1035 | 55 | 25 | 3 | 11.8455 | 7.897 | 5.9227 | 4.7382 | 3.9485 | 3.3844 | 2.9614
WS1054 | 60 | 40 | 4 | 18 | 12 | 9 | 7.2 | 6 | 5.1429 | 4.5
WS1252 | 75 | 50 | 5 | 23.6818 | 15.7879 | 11.8409 | 9.4727 | 7.8939 | 6.7662 | 5.9205
Projected Salt Usage Per Month
All models |  |  |  | 8.4751 | 12.7127 | 16.9502 | 21.1878 | 25.4254 | 29.6629 | 33.9005
(3) ERIE 2400VS SETTINGS
Hardness figure to enter. |  |  |  | 3: 22; 4: French degrees (f)
Capacity figure (default) |  |  |  | 3: 5.2; 4: g/L
The remaining 2 parameters to enter are from the appropriate "media volume" and "Cycle 3" columns above